5 Brian Drive.

Installation Scope of Work

Home Hardware – Holding Tanks

| Prepared For: |  | Prepared By: |
| --- | --- | --- |
| Date: 20-Mar-2025 |  |  |

- TABLE OF Contents

1	General	2

1.1	Notes	2

2	Codes, Standards, and General Requirements	3

2.1	Reference Code Documents	3

2.2	Local Codes	4

3	Installation Guidelines	4

3.1	General	4

3.2	Alignment of Equipment	4

3.3	Shimming and Grouting	5

3.4	Bolting Procedure	5

3.5	Instrument Installation	5

3.6	Piping	6

3.7	Pipe Supports	7

3.8	Gaskets	7

4	Structural Installation guidelines	8

4.1	Notes	8

4.2	Mill Tests	8

4.3	Delivery, Storage, and Handling	8

4.4	Bolting	9

5	Overview of Scope of Work	9

5.1	Structural Installation	9

5.2	Installation of Equipment & Piping	9

6	Demolition Scope of Work	10

7	Installation of Equipment & Piping	10

8	Testing, Cleaning, Commissioning, and Hand Over	11

8.1	Inspection and Cleaning	11

8.2	Quality Control	11

8.3	Pipe Testing	12

9	Appendicies	13

9.1	Appendix A: 3D Model	13

9.2	Appendix B: Pipe Specification and Contrator Supplied Items	13

9.3	Appendix C: P&ID	13

9.4	Appendix D: Isometric Drawings	13

9.5	Appendix E: Vendor Drawings	13

# General

The Contractor is responsible for all work outlined within this document, in its appendices, and otherwise specified by Home Hardware or Element6 Solutions (ELEMENT6). The Contractor shall supply all necessary materials, labour, supervision, tools, equipment, and consumables necessary to complete the work within the designated timeline.

## Notes

The Contractor shall examine the documents and drawings carefully, inspect the site to verify the scope of work, and fully acquaint themselves with the requirements of this division.

    - In the event of discrepancy between the 3D model and other documents, please report the discrepancy to Home Hardware. Generally, the following hierarchy shall be applied:

- Purchase Order Terms and Conditions

- Vendor Drawings and Installation Guidelines

- Scope of Work Package

- Pipe Specification

- P&IDs

- Isometric and Equipment Layout Drawings

- 3D Model

    - The Contractor (including all workers that will be performing on-site work) is required to complete Home Hardware’s Contractor Safety Training, prior to beginning work.

    - The Contractor shall provide all materials for a completed system including miscellaneous supports, gaskets, and bolts.

    - Unless otherwise specified, The Contractor shall supply all necessary materials, labour, supervision, tools, ect. For the satisfactory completion of the work described herein.

    - The Contractor shall supply all necessary equipment and personnel for cleaning after work is completed.

    - The Contractor must obtain a safe work permit prior to commencing work each day.

    - All hot work is to conform with Home Hardware’s hot work procedures.

    - The Contractor shall be responsible for all owner supplied materials until commissioned and turned over in-service to Home Hardware.

    - The Contractor is responsible for installing all equipment and materials.

    - All work is to be performed with care and in a workmanlike manner.

    - The Contractor shall field verify all dimensions before beginning construction and report any changes or discrepancies to Home Hardware.

    - Approval of The Contractor’s procedures, substitutions, drawings, etc, shall not relieve the responsibility for the correctness of details, and compliance with all codes, legal requirements and this scope of work package.

    - The Contractor shall take necessary precautions to safeguard life and property, appropriate to working in a hazardous area.

    - The plant will be in operation while The Contractor is working. The Contractor will have to co-ordinate work with Home Hardware and ensure there are no interruptions to the production schedule due to the construction work.

    - The Contractor must indicate which divisions of work are to be self-completed and which are to be subcontracted.

    - Work is to be completed according to an owner-specified schedule. The schedule will be released to The Contractor with reasonable notice to allow for contractor planning and mobilization. The Contractor is responsible for satisfactory completion within a scheduled timeframe.

    - The Contractor shall remove all debris, scrap, and waste and place it in bins and dumpsters located on site as directed by Home Hardware.

    - Contractor must supply grating clips.

# Codes, Standards, and General Requirements

## Reference Code Documents

- O. Reg. 332/12: Building Code

- The National Building Code of Canada

- CISC - Handbook of Steel Construction

- CISC - Code of Standard Practice

- CAN/CSA S16:19 Limit States Design of Steel Structure

- CAN/CSA G40.21 Structural Quality Steels

- CAN/CSA G164 Hot Dip Galvanizing of Irregularly Shaped Articles

- ASME II: Material Specifications

- ASME B18.2.1: Square and Hex Bolts and Screws (Inches)

- ASME B31.3: Process Piping

- NFPA 77 (2019) – Recommended Practice on Static Electricity

## Local Codes

- Design and fabricate in accordance with federal, provincial, and local codes, and regulations of Burford, Ontario.

- New Piping shall be registered with the TSSA, as required

# Installation Guidelines

## General

    - Equipment shall be installed per supplier’s manuals. Vendor literature shall be consulted to verify that all installation requirements have been fulfilled. Where information regarding equipment installation is not available, The Contractor shall coordinate with Home Hardware to obtain the proper instructions and/or information.

    - The Contractor is responsible for checking clearances around all equipment and shall report any interferences to Element6 Solutions Home Hardware.

    - The Contractor shall tighten all bolts, nuts, screws, ect., restore damaged equipment to its true and original shape, clean and prime all scratches / blemishes and refinish the equipment to match the original finish, all in a neat and workmanlike manner.

    - For offloading, relocation, and installation, The Contractor shall supply all lifting equipment of adequate size to lift and lower the larger items without dragging or dropping, to prevent any damage. The Contractor will check exact equipment dimensions and weights prior to installation.

    - The Contractor shall supply and install all piping, fittings, and pipe supports during installation.

    - The Contractor shall install equipment in the location indicated in the 3D model in Appendix A.

## Alignment of Equipment

    - Align equipment to 1/16” in 10’ vertically and horizontally.

    - Level equipment from the high point of finished floor elevation, or other reference surface by shimming.

## Shimming and Grouting

    - Align and shim all equipment to the elevations and locations shown in the 3D model.

    - Grout all reservoirs, pumps filters, and pipe supports mounted on concreter floors using approved routing materials and methods.

    - Do not apply the grout above the bottom of base plates.

    - Trim the grout neatly to a 45˚ angle before the grout sets.

## Bolting Procedure

    - All flanged joints shall be fitted up so that the gasket contact faces bear uniformly on the gasket and made up with uniform bolt stress.

    - In bolting gasketed flanged joints, bolts shall be torqued to gasket manufacturers specification and torque calves and bolt up procedures.

    - Bolts or stud bolts shall extend completely through the nuts with 3 threads beyond nut face.

    - Studs and nut material shall conform with the pipe/duct specification.

    - Drill holes through support steel to match equipment anchor hole sizes and locations after equipment has been located and aligned except where holes have been provided. All drilled holes shall be painted by The Contractor using zinc-rich primer or to match original equipment manufacturer coating.

    - Use maximum bolt sizes possible when bolting equipment to support steel. Minimum bolt diameter is 1/8” less than the hole diameter.

    - Bolts for the Canty sight glass are to be stainless steel.

    - Use the maximum anchor size which can be installed in the equipment anchoring holes.

## Instrument Installation

    - The Contractor shall install all Owner supplied and Contractor supplied in-line assets and utility pipeline instruments as shown in the model.

    - Supply and install all piping, fittings, gaskets, and valves.

    - Check and ensure that all instruments supplied to, or by The Contractor are of the sizes and types as shown in the model.

    - Installation in accordance with manufacturer’s documentation.

    - ¼” tubing and quick connect fittings to actuated valves shall be supplied by Contractor. Tubing material and specifications to be approved by Home Hardware.

    - All electrical work associated with the installation of the instruments will be done by The Electrical Contractor and is not part of this scope.

    - All instruments shall be handled with care. Any damage to instruments shall be reported immediately to Element6 and Home Hardware.

    - The instruments will be shipped as complete assemblies. Correct mounting position shall be checked prior to installation.

    - All instruments shall be properly oriented to enable ease of access for operation and maintenance.

## Piping

    - The piping system shall be supplied and installed in accordance with ASME B31.3 and owner-supplied pipe specifications (Appendix B). The Contractor shall not use any other piping specifications unless otherwise approved by Home Hardware.

    - All new piping shall be supplied by The Contractor

    - Unless otherwise noted, dimensions are to the centerline of pipe and to the contact face of flange/triclamp.

    - Piping shall be bent only where indicated on the isometric drawings. In all other cases, elbows shall be used.

    - All flanges, threaded ends and other openings shall be protected against damage and dirt by suitable covers of wood or plastic, which are to be bolted or firmly taped to the pipe.

## Pipe Supports

    - All pipe supports shall be supplied and installed by The Contractor. Dimensions shall be field checked by The Contractor and modified to suit each instance.

    - The provision of any structural steel not shown on the drawings or on the reference drawings is the responsibility of The Contractor.

    - Maximum spacing for horizontal piping supports shall be based on nominal pipe size indicated for water usage, as listed below referenced from ASME B31.3. Support spacing exceeding the limits listed shall be approved by Home Hardware:

Table 1: Maximum Pipe Support Spacing

| Nominal Size | Maximum Spacing |
| --- | --- |
| 1” | 6’ |
| 2” – 6” | 8’ - 10’ |
| >6” | 10’ – 12’ |

    - Sag between pipe supports shall not exceed 5/8”.

    - The pipe shall be supported so that no dead weight or strain is transferred to any equipment or instrumentation.

    - All inline instruments and control valves shall be supported independent of pipe unless otherwise noted.

    - Additional miscellaneous steel and pipe supports not shown on the drawings shall be supplied and installed as required.

    - Pipe supports and hangers shall be supported from appropriate foundation or steel suitable for bearing the required load.

## Gaskets

    - Gaskets shall be made of materials compatible with the applicable process fluid and parameters.

    - Gaskets shall conform to ASME B16.20 or ASME B16.21.

    - All gaskets shall be supplied as per piping specifications.

# Structural Installation guidelines

## Notes

    - The Contractor is responsible for the installation of all structural steel.

    - In the case of pipe supports, the model/drawings show general dimensions only and are not for construction. Dimensions are to be field verified before fabrication/installation.

    - Fabrication is not to commence until Home Hardware has approved all fabrication drawings.

## Mill Tests

    - Supply all samples required for inspection and testing and submit copies of mill analysis and test records representative of the materials supplied.

## Delivery, Storage, and Handling

    - Store and handle structural steel to prevent warping and damage of the paint coat.

    - Store the steel on heavy timbers so that they are clear of the ground, contaminates, and muddy areas.

    - Store bolts, other fastenings and welding materials in their original containers, indoors. Keep welding electrodes in warm and dry storage in their sealed protective containers until required for the work. Protect electrodes in open containers from moisture.

## Bolting

    - Install high strength bolts complete with beveled washers as required.

    - Provide friction type or bearing type bolted connections on drawings.

    - Fasten high tensile bolts by means of turn-of-the-nut method or using calibrated wrench. Verify bolt tension with a testing wrench. All high strength bolts shall be tightened to the minimum bolt tension given in Table 7 of CAN/CSA-S16.1-M-89, in accordance with clause 23.5 or 23.6.

    - Nuts on A307 bolts and on anchor bolts shall be tightened to an amount corresponding to the full effort of a person using a spud wrench. Nuts shall be prevented from working loose using lock washers or lock nuts for A307 bolt, and lock washers, lock nuts, jam nuts, thread burring, double nuts or welding for anchor bolts.

# Overview of Scope of Work

## Structural Installation

    - Erection of one (1) structural platform in 2 phases. Phase 1 is to be completed in the week of August 18th. The second phase will be completed in October.

    - The platform is to be installed per the provided structural drawings.

## Installation of Equipment & Piping

    - Installation of two (2) diaphragm and pump skid.

    - Installation of four (4) bag filters.

    - Installation of 2 tanks.

    - Installation of two (2) agitators.

    - Installation of tank instrumentation.

    - Mechanical installation of all new process and utility piping. Including piping, fittings, valves, and instrumentation as shown in the P&IDs (Appendix C), Isometric Drawings (Appendix D), and 3D model (Appendix A).

# Demolition Scope of Work

    - Line breaking and cleaning by others.

    - Prior to demolition, The Contractor shall verify that all lines have been cleaned.

# Installation of Equipment & Piping

    - All equipment installation to adhere to guidelines specified in Section 3.0.

    - Equipment locations to be as specified in the 3D model, exact locations and positioning shall be provided once bid has been awarded.

    - Positioning of all major components of each system to be verified prior to any anchoring and/or grouting. The entire system shall be “roughed in” before any equipment is anchored in place.

    - Wherever available, vendor supplied equipment installation instructions (Appendix E) shall be strictly adhered to.

    - The Contractor shall provide instrument connections in the piping systems such as tees, couplings, etc.

    - The Contractor shall install all pipe and equipment mounted instrument isolation valves.

    - The Contractor shall install all pipe, valves, piping, and insulation, as required.

    - The Contractor shall be responsible for a service test with flush product of all piping systems which are part of this project.

    - All new piping shall be installed at reasonable distance from existing piping, instrumentation, emergency vents, etc. for ease of maintenance and replacement.

    - The Contractor shall supply and install flashing around equipment and piping which may penetrate the roof, walls or grating.

    - Tie in all pipes to tie points indicated. Tie point size and location to be verified by The Contractor during site visit.

    - Install screwed caps or blind flanges and gaskets at the open end of all vents and drain valves and future tie points.

    - Wherever possible, piping and valve assembly is to be done off-site, prior to construction to minimize construction and installation time.

    - All piping fabricated shall be in accordance with the requirements of the latest revisions of ASME B31.3 and the requirements of this standard.

    - The P&IDs indicate “to and from” routing, identification number for each line. Their intent is to provide a basis for field checks of continuity and completeness of piping systems.

    - The Contractor shall field run all utility pipe routing. Tie points to existing headers, routing, and pipe support location are to be approved by Home Hardware before construction begins.

    - All piping fabricated in accordance with this standard shall also meet the requirements of local and federal regulations.

    - The Contractor shall indicate to Home Hardware if any additional break flanges, field welds, or pipe supports are required for installation purposes. Work is not to proceed on the indicated line until Home Hardware has reviewed and approved the alteration.

# Testing, Cleaning, Commissioning, and Hand Over

## Inspection and Cleaning

    - Advise Home Hardware when the system is considered complete and ready for cleaning so that a visual inspection by Home Hardware may be performed.

    - Critical punch list items identified by Home Hardware must be corrected by The Contractor prior to cleaning.

## Quality Control

    - Test to verify components are functional and properly adjusted.

    - Visually inspect system and conduct dry run test.

    - Maintain records of inspections and tests. Indicate nature and number of deficiencies found, quantities approved and rejected, and nature of corrective actions taken. On request, supply copies of inspection and test data.

    - Provide notification not less than 5 working days prior to conducting inspection or testing required by this section.

    - Reviews, inspections, and witnessing does not relieve The Contractor of responsibility to comply with this section

## Pipe Testing

    - A hydrostatic leak test is required after pipe installation to be done with a flushing product.

    - All on-site pipe testing shall be executed as agreed with Home Hardware in accordance with ASME B31.3 and local requirements. The Contractor shall submit a pipe test schedule to indicate the timing and identification of piping to be tested.

    - Notify Home Hardware at least 48 hours prior to the testing so that he may be present to witness the tests.

    - Equipment not to be subjected to test pressure shall be disconnected or otherwise isolated. Valves may be used if, including closing mechanism, is suitable for the test pressure.

    - The Contractor shall supply Home Hardware with a complete record of all pipe tests once testing is completed.

    - All  protective equipment shall be tested to verify that they are in good mechanical condition; of adequate capacity, effectiveness, and reliability of operation for the service in which they are employed; functioning at the correct pressure; and properly installed and protected from foreign materials or other conditions that might prevent proper operation.

    - The Contractor shall completely dry all lines after testing.

# Appendicies

## Appendix A: 3D Model

## Appendix B: Pipe Specification and Contrator Supplied Items

## Appendix C: P&ID

## Appendix D: Isometric Drawings

## Appendix E: Vendor Drawings